## ReadMe
D6/D7 — SES Validation & Post-Processing Workbook
Memorial Tunnel TVS ¦ STN-MT-PP-007 Rev A ¦ Synoptic CFD
What this is | A repeatable pipeline that compares SES-predicted airflow/velocity/temperature against measured Memorial Tunnel data, and reports the error used as the validation margin in the Final Report (D9).
Workflow | 1) Run SES locally -> .PRN. 2) parse_prn.py converts .PRN -> *_parsed.csv (SI units). 3) Drop parsed CSVs next to this workbook. 4) Refresh (VBA button or manual paste) -> Comparison + Dashboard update.
Sheets | ReadMe · SES_Data (parsed) · Measured_Data · Comparison · Dashboard · VBA_Instructions
Colour key | Blue = input/paste area. Black = formula. Green = cross-sheet link. Yellow = key result.
Units | All SI. SES .PRN is Imperial; parse_prn.py converts (CFM->m3/s, FPM->m/s, F->C).
Data shown | The reference 100 MW run (Test 615B, MT-T615B-R3-3) is preloaded as a worked example. Replace with your own runs via the refresh path.

## SES_Data
Section | Distance (m) | Flow (m3/s) | Velocity (m/s) | Temp (C)
1 | 10.7 | 176.1126 | 4.7772 | 5.111
2 | 32 | 176.1126 | 2.955 | 5.222
3 | 53.4 | 176.1126 | 2.955 | 5.333
4 | 79.4 | 176.1126 | 2.955 | 5.444
5 | 98.1 | 176.1126 | 2.955 | 5.444
6 | 112.2 | 176.1126 | 2.955 | 5.556
7 | 133.5 | 176.1126 | 2.955 | 5.611
8 | 154.9 | 176.1126 | 2.955 | 5.722
9 | 177.6 | 176.1126 | 2.955 | 5.778
10 | 193 | 176.1126 | 2.955 | 5.833
11 | 207 | 176.1126 | 2.955 | 5.889
12 | 228.3 | 176.1126 | 2.955 | 6
13 | 249.7 | 176.1126 | 2.955 | 6.056
14 | 272.5 | 176.1126 | 2.955 | 6.167
15 | 288.1 | 176.1126 | 2.955 | 6.167
16 | 302.1 | 176.1126 | 2.955 | 6.222
17 | 323.4 | 176.1126 | 2.955 | 6.333
18 | 344.8 | 176.1126 | 2.955 | 6.389
19 | 367.5 | 176.1126 | 2.955 | 6.444
20 | 382.9 | 176.1126 | 2.955 | 6.556
21 | 393.5 | 176.1126 | 2.955 | 6.611
22 | 411.5 | 176.1126 | 2.955 | 6.667
23 | 432.8 | 176.1126 | 2.955 | 6.722
24 | 454.2 | 176.1126 | 2.955 | 6.778
25 | 469.6 | 176.1126 | 2.955 | 6.778
26 | 477.7 | 176.1126 | 2.955 | 6.833
27 | 491.7 | 176.1126 | 2.955 | 6.944
28 | 513 | 176.1126 | 2.955 | 7
29 | 534.4 | 176.1126 | 2.955 | 7.056
30 | 555.4 | 176.1126 | 2.955 | 7.056
31 | 569.1 | 176.1126 | 2.955 | 7.111
32 | 583.1 | 176.1126 | 2.955 | 7.167
33 | 604.4 | 176.1126 | 2.955 | 416.056
34 | 625.8 | 176.1126 | 2.955 | 404.278
35 | 647.1 | 176.1126 | 2.955 | 399
36 | 662.6 | 176.1126 | 2.955 | 395.444
37 | 670.9 | 176.1126 | 2.955 | 384.444
38 | 684.9 | 176.1126 | 2.955 | 373.889
39 | 706.2 | 176.1126 | 2.955 | 363.722
40 | 727.6 | 176.1126 | 2.955 | 354.167
41 | 748.6 | 176.1126 | 2.955 | 351.111
42 | 762.4 | 176.1126 | 2.955 | 341.778
43 | 776.4 | 176.1126 | 2.955 | 332.778
44 | 797.7 | 176.1126 | 2.955 | 323.056
45 | 820.4 | 176.1126 | 4.7772 | 315.611

## Measured_Data
Measured quasi-steady airflow (mean of last 25% of record)
Loop | Airflow (m3/s)
Loop 214 | 229.28
Loop 209 | 224.64
Loop 208 | 263.91
Loop 207 | 259.07
Loop 307 | 253.76
Loop 305 | 277.19
Loop 304 | 169.42
Loop 302 | 63.83
Loop 301 | 207.88
Loop 202 | 220.93

## Comparison
SES vs Measured — Quasi-Steady Airflow Validation
Each measured loop (quasi-steady mean, last 25% of record) vs the SES bulk airflow at quasi-steady. Single-bore tunnel: airflow is ~uniform along the length.
Loop / location | Measured (m3/s) | SES (m3/s) | Error (m3/s) | Error (%) | Within +/-15%?
Loop 214 | 229.28 | 176.1126 | -53.1674 | -23.19% | NO
Loop 209 | 224.64 | 176.1126 | -48.5274 | -21.6% | NO
Loop 208 | 263.91 | 176.1126 | -87.7974 | -33.27% | NO
Loop 207 | 259.07 | 176.1126 | -82.9574 | -32.02% | NO
Loop 307 | 253.76 | 176.1126 | -77.6474 | -30.6% | NO
Loop 305 | 277.19 | 176.1126 | -101.0774 | -36.47% | NO
Loop 304 | 169.42 | 176.1126 | 6.6926 | 3.95% | YES
Loop 302 | 63.83 | 176.1126 | 112.2826 | 175.9% | NO
Loop 301 | 207.88 | 176.1126 | -31.7674 | -15.28% | YES
Loop 202 | 220.93 | 176.1126 | -44.8174 | -20.29% | NO
Loop mean (measured) | 216.991 | 176.1126
Overall validation error (SES vs measured mean) |  |  |  | -18.84%
Mean absolute % error (per loop) |  |  |  | 39.26%
Interpretation: SES under-predicts bulk airflow (typical for 1-D longitudinal fire modelling). The magnitude of this error is carried as a conservative safety margin on ventilation capacity in the Final Report (D9).

## Dashboard
Validation Dashboard — 100 MW (Test 615B)
Longitudinal velocity & temperature profiles from SES; airflow comparison vs measured.
Design critical velocity (100 MW) = 3.19 m/s (from D2). Sections upstream of the fire should meet or exceed this.

## VBA_Instructions
VBA Automation — Import & Use
This workbook ships with two VBA modules (delivered as .bas files):
• Module_RefreshValidation.bas — imports parsed SES CSV + measured CSV, refreshes Comparison & Dashboard.
• Module_BatchParse.bas — shells parse_prn.py over a folder of .PRN files, then loads results.
To install (one time):
1. Save this workbook as .xlsm (File > Save As > Excel Macro-Enabled Workbook).
2. Press Alt+F11 to open the VBA editor.
3. File > Import File… and select each .bas module.
4. Close the editor. The macros appear under Developer > Macros.
To use:
• RefreshValidation: prompts for the parsed SES CSV and the measured CSV, then repopulates SES_Data / Measured_Data and recalculates.
• BatchParse: prompts for a folder; runs the Python parser on every .PRN and imports the newest result.
Note: BatchParse requires Python on PATH and parse_prn.py in the same folder. If macros are blocked by policy, use the manual path: paste the *_parsed.csv columns into SES_Data (cols C–E) and the workbook recalculates automatically.